## Controller_Limits
Controller_Model | System_Type | Supports_NIO | Supports_FIO | Max_NIU_Nodes | Max_NIO_IO_Units | Max_Safety_Nodes | Max_FIO_Modules | Max_Dual_Red_Modules
S2SC70S | Safety | Yes | Yes | 32 | 108 | 13 | 110 | 55
S2SC70D | Safety | Yes | Yes | 32 | 108 | 13 | 110 | 55
SCS60S | Safety | No | Yes | 0 | 0 | 13 | 110 | 55
SCS60D | Safety | No | Yes | 0 | 0 | 13 | 110 | 55
SCS50S | Safety | No | Yes | 0 | 0 | 9 | 78 | 39
SCS50D | Safety | No | Yes | 0 | 0 | 9 | 78 | 39

## Mounting Rule
Node Type | Node No | Slot | Type
SNU | >1 | 1 | IOM
SNU | >1 | 2 | IOM
SNU | >1 | 3 | IOM
SNU | >1 | 4 | IOM
SNU | >1 | 5 | IOM
SNU | >1 | 6 | IOM
SNU | >1 | 7 | IOM
SNU | >1 | 8 | IOM
SNU | >1 | 9 | SSB401
SNU | >1 | 10 | SSB401
SNU | >1 | 11 | SPW482
SNU | >1 | 12 | SPW482
SCU_Without_ESB | Node 1 Only | 1 | IOM
SCU_Without_ESB | Node 1 Only | 2 | IOM
SCU_Without_ESB | Node 1 Only | 3 | IOM
SCU_Without_ESB | Node 1 Only | 4 | IOM
SCU_Without_ESB | Node 1 Only | 5 | IOM
SCU_Without_ESB | Node 1 Only | 6 | IOM
SCU_Without_ESB | Node 1 Only | 7 | IOM
SCU_Without_ESB | Node 1 Only | 8
SCU_Without_ESB | Node 1 Only | 9 | SSB401
SCU_Without_ESB | Node 1 Only | 10 | SSB401
SCU_Without_ESB | Node 1 Only | 11 | SPW482
SCU_Without_ESB | Node 1 Only | 12 | SPW482
SCU_With_ESB | 1 | 1 | IOM
SCU_With_ESB | 1 | 2 | IOM
SCU_With_ESB | 1 | 3 | IOM
SCU_With_ESB | 1 | 4 | IOM
SCU_With_ESB | 1 | 5 | IOM
SCU_With_ESB | 1 | 6 | IOM
SCU_With_ESB | 1 | 7 | SEC401
SCU_With_ESB | 1 | 8 | SEC401
SCU_With_ESB | 1 | 9 | SSB401
SCU_With_ESB | 1 | 10 | SSB401
SCU_With_ESB | 1 | 11 | SPW482
SCU_With_ESB | 1 | 12 | SPW482

## IO_Module_Catalog
Family | Module | IO_Type | Signal_Type | Nominal_Channels | Supports_HART | Description | Wiring | Ambient_Max_C | Usable_Channels | CoeffA_Single | CoeffA_Dual | CoeffB_Single | CoeffB_Dual | Remarks | Suffix_Signal_Type | Suffix_Temperature | Suffix_Explosion | Suffix_Redundancy | Model_Number_Pattern | Example_Full_Model
FIO | SAI143-S | AI | 4-20mA | 16 | No | Analog Input Module (4 to 20mA, 16-ch, module isolation) – Standard type | 2-wire | 60 | 16 | 3 | 5 | 22 | 25 | Normal | S | 3 | S | N | SAI143-S-{SIG}{TEMP}{EX}{RED} | SAI143-S-S3SN
FIO | SAI143-S | AI | 4-20mA | 16 | No | Analog Input Module (4 to 20mA, 16-ch, module isolation) – Standard type | 2-wire | 65 | 14 | 3 | 5 | 22 | 25 | Derated | S | 3 | S | N | SAI143-S-{SIG}{TEMP}{EX}{RED} | SAI143-S-S3SN
FIO | SAI143-S | AI | 4-20mA | 16 | No | Analog Input Module (4 to 20mA, 16-ch, module isolation) – Standard type | 2-wire | 70 | 10 | 3 | 5 | 22 | 25 | High Temp | S | 3 | S | N | SAI143-S-{SIG}{TEMP}{EX}{RED} | SAI143-S-S3SN
FIO | SAI143-S | AI | 4-20mA | 16 | No | Analog Input Module (4 to 20mA, 16-ch, module isolation) – Standard type | 4-wire | 65 | 16 | 3 | 5 | 4 | 7 |  | S | 3 | S | N | SAI143-S-{SIG}{TEMP}{EX}{RED} | SAI143-S-S3SN
FIO | SAI143-S | AI | 4-20mA | 16 | No | Analog Input Module (4 to 20mA, 16-ch, module isolation) – Standard type | 4-wire | 70 | 12 | 3 | 5 | 4 | 7 |  | S | 3 | S | N | SAI143-S-{SIG}{TEMP}{EX}{RED} | SAI143-S-S3SN
FIO | SAI143-H | AI | 4-20mA | 16 | Yes | Analog Input Module (4 to 20mA, 16-ch, module isolation) – HART type | 2-wire | 60 | 16 | 3 | 6 | 25 | 29 | HART | S | 3 | S | N | SAI143-H-{SIG}{TEMP}{EX}{RED} | SAI143-H-S3SN
FIO | SAI143-H | AI | 4-20mA | 16 | Yes | Analog Input Module (4 to 20mA, 16-ch, module isolation) – HART type | 2-wire | 65 | 14 | 3 | 6 | 25 | 29 |  | S | 3 | S | N | SAI143-H-{SIG}{TEMP}{EX}{RED} | SAI143-H-S3SN
FIO | SAI143-H | AI | 4-20mA | 16 | Yes | Analog Input Module (4 to 20mA, 16-ch, module isolation) – HART type | 2-wire | 70 | 8 | 3 | 6 | 25 | 29 |  | S | 3 | S | N | SAI143-H-{SIG}{TEMP}{EX}{RED} | SAI143-H-S3SN
FIO | SAI143-H | AI | 4-20mA | 16 | Yes | Analog Input Module (4 to 20mA, 16-ch, module isolation) – HART type | 4-wire | 65 | 16 | 3 | 6 | 5 | 10 |  | S | 3 | S | N | SAI143-H-{SIG}{TEMP}{EX}{RED} | SAI143-H-S3SN
FIO | SAI143-H | AI | 4-20mA | 16 | Yes | Analog Input Module (4 to 20mA, 16-ch, module isolation) – HART type | 4-wire | 70 | 12 | 3 | 6 | 5 | 10 |  | S | 3 | S | N | SAI143-H-{SIG}{TEMP}{EX}{RED} | SAI143-H-S3SN
FIO | SDV144-S | DI | 24VDC | 16 | No | Digital Input Module (24V DC, 16 channels, module isolation) | NA | 65 | 16 | 2 | 4 | 2 | 4 |  | S | 3 | S | N | SDV144-S-{SIG}{TEMP}{EX}{RED} | SDV144-S-S3SN
FIO | SDV144-S | DI | 24VDC | 16 | No | Digital Input Module (24V DC, 16 channels, module isolation) | NA | 70 | 12 | 2 | 4 | 2 | 4 |  | S | 3 | S | N | SDV144-S-{SIG}{TEMP}{EX}{RED} | SDV144-S-S3SN
FIO | SDV541-S | DO | 24VDC | 16 | No | Digital Output Module (24V DC, 16 channels, module isolation) | NA | 60 | 16 | 3 | 6 | 5 | 7 |  | S | 3 | S | N | SDV541-S-{SIG}{TEMP}{EX}{RED} | SDV541-S-S3SN
FIO | SDV541-S | DO | 24VDC | 16 | No | Digital Output Module (24V DC, 16 channels, module isolation) | NA | 65 | 12 | 3 | 6 | 5 | 7 |  | S | 3 | S | N | SDV541-S-{SIG}{TEMP}{EX}{RED} | SDV541-S-S3SN
FIO | SDV541-S | DO | 24VDC | 16 | No | Digital Output Module (24V DC, 16 channels, module isolation) | NA | 70 | 10 | 3 | 6 | 5 | 7 |  | S | 3 | S | N | SDV541-S-{SIG}{TEMP}{EX}{RED} | SDV541-S-S3SN
NIO | S2MMM843 | AI, DI, DO, AO | Mixed | 16 | No | Analog and Digital I/O Module (16-channels, isolated) | Configurable | 70 | 16 | 0 | 0 | 0 | 0 | N-IO | SS | 3 | S | N | S2MMM843-{SIG}{TEMP}{EX}{RED} | S2MMM843-SS3SN
NIO | S2MDV843 | DI | Digital | 16 | No | Digital I/O Module (16-channels, isolated) | Configurable | 70 | 16 | 0 | 0 | 0 | 0 | N-IO | S | 3 | S | N | S2MDV843-{SIG}{TEMP}{EX}{RED} | S2MDV843-S3SN
NIO | S2BN1D | Baseplate | NA | 0 | No | Baseplate with disconnecting terminal (for N-IO, 16-channel) | NA | 70 | 0 | 0 | 0 | 0 | 0 |  | SS | 3 | S | N | S2BN1D-{SIG}{TEMP}{EX}{RED} | S2BN1D-SS3SN
NIO | S2BN4D | Baseplate | NA | 0 | No | Base Plate for Barrier (for N-IO, MTL Barrier) | NA | 70 | 0 | 0 | 0 | 0 | 0 |  | SS | 3 | S | N | S2BN4D-{SIG}{TEMP}{EX}{RED} | S2BN4D-SS3SN
NIO | S2BN5D | Baseplate | NA | 0 | No | Base Plate for Barrier (for N-IO, P&F Barrier) | NA | 70 | 0 | 0 | 0 | 0 | 0 |  | SS | 3 | S | N | S2BN5D-{SIG}{TEMP}{EX}{RED} | S2BN5D-SS3SN

## NIO_System_Constraints
Constraint | Value | Units | Remarks
Max_NIO_Units_per_NIU | 6 | Units
Max_Channels_per_NIU_System | 96 | Channels | 1 NIU + 6 N-IO
Max_AO_per_Module | 8 | Channels
Max_Channel_Current | 0.66 | A
Max_2Ch_Parallel_Current | 1.3 | A
Max_3Ch_Parallel_Current | 2 | A

## NIO_Ambient_Current_Limits
Ambient_Min_C | Ambient_Max_C | Max_Total_Current_A
-40 | 40 | 10.56
40 | 50 | 9.71
50 | 60 | 8.85
60 | 70 | 8